## Slide 1: An Active Command Mediation System for Securing Remote Control Interface of Electrical Substations (IEEE SmartGridComm 2016)
Daisuke Mashima
Prageeth Gunathilaka
Binbin Chen
Version 2, WGT
Acknowledgment:
The work was in part funded under the Energy Innovation Research Programme (EIRP, Award No. NRF2014EWT-EIRP002-040), administrated by the Energy Market Authority (EMA) and in part by the research grant for the Human-Centered Cyber-physical Systems Programme at the Advanced Digital Sciences Center from Singapore’s Agency for Science, Technology and Research (A*STAR). The EIRP is a competitive grant call initiative driven by the Energy Innovation Programme Office, and funded by the National Research Foundation (NRF).

## Slide 2: Outline
Motivation: Need for additional layer of security for electrical substations
Related work
Design of Active Command Mediation (A*CMD) framework
Concrete mitigation mechanism on A*CMD
Simulation results
Conclusions

## Slide 3: Electrical Substations
A substation is a crucial component of an power grid system delivering electricity from generation to loads.
  Voltage transformation, switching, fault isolation, voltage regulation etc.
Between the generating station and consumer, electric power may flow through several substations at different voltage levels.
  Over 10,000 transmission/distribution substations in Singapore

## Slide 4: Modernization of Substations
Adoption of standard technologies such as IEC 60870-5-104 and IEC 61850 for remote control and automation
IEC 61850-90-2 TR: Communication networks and systems for power utility automation –
Part 90-2: Using IEC 61850 for the communication between substations and control centres - Page 10

## Slide 5: Remote Control Use Cases
Power shedding
  To handle over generation from renewables, the control center controls the output from the generation and/or makes it offline
Voltage regulation
  Shunt reactors/capacitors are controlled (either on/off or variable setpoints) to manage voltages according to the change in loads
Topology control
  To optimize generation and transmission cost, power grid topology is changed.

## Slide 6: Security Risks
Attack from network
  Insecure deployment of IEC 60870 and 61850 is vulnerable against man-in-the-middle attacks, replay attacks, etc.
    B. Kang, P. Maynard, K. McLaughlin, S. Sezer, F. Andren, C. Seitl, F. Kupzog, and T. Strasser. Investigating cyber-physical attacks against iec 61850 photovoltaic inverter installations. In Emerging Technologies & Factory Automation (ETFA), 2015 IEEE 20th Conference on, pages 1–8. IEEE, 2015.
    P. Maynard, K. McLaughlin, and B. Haberler. Towards understanding man-in-the-middle attacks on iec 60870-5-104 scada networks. In Proceedings of the 2nd International Symposium on ICS & SCADA Cyber Security Research 2014, pages 30–42. BCS, 2014.
Attack from the control center
  Disgruntled insiders
  Malware
  Physical / Cyber intruders

## Slide 7: Threats Are Real!
http://theconversation.com/cyberattack-on-ukraine-grid-heres-how-it-worked-and-perhaps-why-it-was-done-52802
http://realtimeacs.com/wp-content/downloads/pdfs/House-Hearing-10-17-Final.pdf
Traditional trust assumption on the control center is no longer valid.
We need additional layer(s) of security to minimize physical impact of cyber attacks!

## Slide 8: Related Work
Firewall, IDS, Anti-virus, user authentication, access control etc.
  Once the control center becomes malicious, many of these are not fully effective.
  Our work is intended to be complementary to these measures.
Runtime semantic security analysis by Lin et al. [TSG2016]
  Shares threat model
  Evaluate outcome of control commands in a centralized manner to detect attacks
  They chose command-reversing approach, which may not be always suitable.
  Our scheme can be used with their attack detection system.

## Slide 9: Active Command Mediation
Add additional-layer of security for securing remote control interface of substation
  Inspect and “pre-process” incoming remote control commands
    Should work autonomously
  Can not be bypassed
  Minimal dependency on external systems
Practically-deployable solution
  Require minimal change on existing infrastructure
  Add minimal overheads

## Slide 10: Autonomous Command-delaying
Attacker
Proxy 1,…,n
Control
Center
IED1
IED2
IED3
IEDn
d1
d2
d3
dn
Execute Control
t1
Attempt Cancelaltion
t0
Send malicious commands
Command Ack
Attack detection system at the control center is assumed.
E.g., Hui Lin, Adam Slagell, Zbigniew Kalbarczyk, Peter W. Sauer, and Ravishankar K. Iyer, "Runtime Semantic Security Analysis to Detect and Mitigate Control-related Attacks in Power Grids," in IEEE Transactions on Smart Grid)
The number of attack commands executed is reduced, and thereby the resulting impact of attacks is also mitigated.

## Slide 11: How Much Delay Can We Add?
IEEE PES Guideline
  Communication between an external control center and substation:
    normally greater than 100ms
  Communication for line sectionalizing:
    5 seconds
  Communication for load shedding:
    10 seconds
  Communication for transfer switching:
    1 second

## Slide 12: How Should Add Delay?
Option 1: Constant, long-enough delay
Option 2: Probabilistically-added constant delay
Option 3: Continuously-random delay(Future Work)
Probability of successful mitigation
  - Detection & Response Time: 620ms
  - Option 2: 75% & 90% delay probability
  - Option 3: Uniform
  Triangular with peak at
  delay upper bound
  Triangular with peak at 0

## Slide 13: Setup for Simulation
PowerWorld Simulator
  Transient stability analysis
  GSO 37-bus system
    57 transmission lines
Simulate attacks against circuit breakers
  Issue open commands to randomly selected circuit breakers
Metrics of attack impact on power grid
  Voltage violation
  Frequency violation
  Reduction in load (Unserved Load)
37-bus system on PowerWorld

## Slide 14: Simulation Results
Over 90% mitigation in # of buses with voltage violation and unserved load
Even with practical attack detection accuracy (e.g., 80-90%), the proposed scheme is still expected to offer significant mitigation.
Voltage Violation (20%)
Unserved Load

## Slide 15: Preliminary Study of Acceptable Delay
Simulated a case requiring power shedding
  Significantly increased generation MW of 3 out of 9 generators in 37-bus system
Delaying recovery controls up to 5.5 seconds did not cause any violation based on WECC criteria.
Even with tighter criteria (0.2Hz deviation), the recovery can be delayed up to 2 seconds.

## Slide 16: Conclusions
Proposed and evaluated active command mediation approach with autonomous command-delaying
  Effectively offers additional layer of security for substations
  Can be introduced with minimal change on existing infrastructure
  Is compatible with widely-used standards
  Can potentially mitigate the impact of malicious remote control commands by 90+%
Future Work
  Investigation on other delaying strategies
  Context-aware, fully-autonomous command mediation system

## Slide 17: Thank you very much!
Questions?
SoftGrid: Software-based Smart Grid Testbed for Evaluating Substation Cybersecurity Solutions
  Companion paper was published at ACM CPS-SPC 2016
  Available as an open-source project under GPL
    Web: https://www.illinois.adsc.com.sg/softgrid/
    Email: softgrid@adsc.com.sg